## LEME EE-ENR
LEME ATTENUATION - SUNREF III - VERSION 2 - Date of Issue: 10 septembre 2020
N°Ref | Date of issue : 10/09/2020 | Objective | Applications | Minimum Performance Criteria/Minimum requirements | International Reference Standards | Estimated pay back time short term : 2-4 years, medium term: 4-6years, long term : 6-8 years (*) | Comments | Visual Example
A. Improve thermal performances of building enveloppe
A.1. | Roofs and walls: retrofiting or new building
A.1.1. | Insulated metal Panels Polyurethane /polycyanurate foam , Extruded polystyrene, Glass wool | Improvment of roof and wall insulation on open framing structures | Existing or new industrial buildings(example : air conditionned production plants, warehouses) | Roof : U< 0,4 W/m2 °C , Walls : U<0,5 W/m2 °C + Reflective or clear colored external coating | CE MARK, KEYMARK, ACERMI,ASTM C518 | short/medium term | Roof is one the main source of cold losses in a air conditionned office or apartment buildings, or air conditionned storages or warehouses ; insulation of a non insulated roof reduces roof cold losses up to 70 %
A.1.2. | Extruded or expanded polystyrene panels, polyurethane panels, spray polyurethane foam , glass wool, rock wool panels or rolls | Improvment of roof insulation on concrete flat roofs and walls | All air conditionned buildings : Offices or apartment buildings, hotels hospitals, production plants... | Roof : U< 0,4 W/m2 °C , under the waterproof covering Walls : U<0,5 W/m2 °C | CE MARK, KEYMARK, ACERMI EN 13 164 | Medium term
A.2. | Windows
A.2.1. | Double-glazing window with low SHGC glass | Improvment of thermal transfert through windows | New or retrofit of all kind of air-conditionned buildings; windows exposed to direct sunshine | Global U factor ≤ 2 W/m2°K Low E coating SHGC (solar heat gain coefficient)<0,5 | CE Marking as per EN ISO 10077-1 | Medium term | Wood, PVC or metal frame . When metal frame, il is necessary to plan thermal ruptors to avoid thermal bridges. Considering the climate of Mauritius, it is necessary to favor the reduction of the solar factor by coloured or reflective glazing on the windows directly exposed to the sun.
A.2.2. | Adhesive film sticked on existing windows for reducing the heat transfer in the building | Reduction of thermal transfert through windows | Retrofit of all kind of air-conditionned buildings; windows exposed to direct sunshine | Solar energy reflection >50 % |  | Short term | Adhesive fim Is a fast and economic measure to reduce thermal transfer by direct sun radiation. However, The life expectancy of this equipment is short. The solar reflection ratio should be verified and certified before being introduced on the market. A technical data sheet has to be produced by the project investor with a full technical description
A.2.3. | External Shading devices : blinds, window covers , Horizontal or vertical sun protections in facade | Protection against direct sunshine (panels or other protecxtion devices) | New or retrofit of all kind of air-conditionned buildings; protection type depends of the sunshine exposure | To avoid the direct sunshine on the more exposed facade (s) in all season. The coverage ratio of the sunshine protection devices will be under 50%of the total surface in most cases. |  | Medium term | The implementation of solar shading devices on windows is the most effective way to reduce the thermal contributions on facades exposed to the direct solar radiation. Type of shading device depends on the orientation of facades ; Protections are rather blackout type for facing east and west windows to raising solar radiations, and to overhanging type for the facing north windows. The protection panels should be designed with the best implementation efficiency by the architects to get the best protection (in case of Greenfield project). No need to cover all the facades of the buiding.
B | Improve HVAC&Refrigeration System performances
B.1. | Individual and medium scale air conditionning systems up to 100 kW
B.1.1. | Monosplit air cooled with inverter P cooling <20 KW. Monosplit cooling power for households should be under 5,0 kW/unit | Reduce the electric consumption by replacing '' no inverter'' air conditioners | For small air conditionned spaces (housing, offices, retail stores….) | At least Energy Efficiency class : SEER > 5,10 for Class A, or Class A+ ''mass market''. This is the base- line. See comments for the highest energy SEER on the market. | Commission Regulation (EU) No 626/2011 supplementing Directive 2010/30/EU EN 814-2/3 (E 36-104-2/3) | Short/medium term | Equipment of Class A and A+ are eligible as a ''mass market'' basic option (energy savings being evaluated in comparison with existing AC units in case of revamping to achieve the 20% target). Products corresponding to the Class A++ with SEER of 6,2, if available on the market to be promoted but not a required condition in all cases . Class A+++ available on the market with SEER of 8,5 are more recent and could also be promoted with the same approach. In all cases, energy efficinecy should be at least 20%.
B1,2 | Multisplits air cooled with inverters and with an unique extenal unit up to 100 kW | Reduce the electric consumtion by replacing air-conditioners in the configuration of several monosplit units in the same building) with the inverter design. By a diffrent design (only one outdoor equipment) | For buildings requiring several units (5 units maximum) in small scale offices or housing) | At least Energy Efficiency class : SEER > 5,10 fo Class A, Class A+ mass market. Products Class A++ or A+++ if available on the market could be promoted. | Commission Regulation (EU) No 626/2011 supplementing Directive 2010/30/EU EN 814-2/3 (E 36-104-2/3) | Short/medium term | Equipment of Class A and A+ are eligible as a ''mass market'' basic option (energy savings being evaluated in comparison with existing AC units in case of revamping to achieve the 20% target). Products corresponding to the Class A++ withSEER of 6,2, if available on the market to be promoted but not a required condition in all cases . Class A+++ available on the market with SEER of 8,5 are more recent and could also be promoted with the same approach. In all cases, energy efficinecy should be at least 20%.
B.2. | Medium range air conditionning systems above 100 kW
B.2.1. | Variable refrigerant flow (VRF) ou variable refrigerant volume (VRV) units above 100 KW | Reduce the electric consumption by replacing existing monosplit, multisplit or small chilled water-air conditionned systems. The design is either under the '' variable refrigerant flow or variable refrigerant volume'' VRF ou VRV concept for systems above 100 kW in most cases. | For medium size buildings, up to 40 rooms (housing, offices, hotels, hospitals…) | SEER ≥ 5,1 VSD ; or varaible speed drive | EU IPPC BAT EE, US DOE EN 814-2/3 (E 36-104-2/3) | Short/medium term | VRF/ VRV systems are a matched combination of up to 40 indoor fan coil units to a single outdoor condensing unit connected only by refrigerant piping and wiring. Each fan coil unit can be independently controlled by varying the refrigerant flow or volume, and in doing so varying capacity being delivered to each zone; making it one of the most effective and efficient systems available ; Energy savings of up to 30% are predicted over comparable unitary equipment. A target ratio of 25% energy savings is seen acceptable on usual projects.
B.3. | Efficient refrigeration systems
B.3.1. | Air cooled high efficiency chillers | Reduce electricity consumption of chillers and pumps by replacing existing air cooled or water cooled chillers | Large public and private air conditionned office buildings, hotels, hospitals | Eurovent class A EER> 3,1 or Inverter ESEER >4,5 Hydrocarbon HFC refrigerants only | Eurovent | Medium term | Reducing electricity consumption by improving performance of chilled water system including chillers, cooling towers, pumps, energy storage . Energy savings can be obtained by replacing chillers with à higher ESEER (higher Eurovent classification), higher efficiency cooling towers (evaporative or semi-evaporative, fans with VSD), revamping pumps with a more efficient motor IE3 or IE2 vs IE1, and adding variable speed drive (VSD) ; in addition off these energy efficient implementations, enregy savings is generally up to 20 % than performances of an usual chilled water system. Free energy produced by solar panels for generating heat to absorption cooling equipments have been proved having very low SEER on several projects (SEER below 2). Investors should be aware of these poor results before adopting this cooling technology (design simulation need to be done to check the expected performance).
B.3.2. | Water cooled high efficiency chillers. And water cooled chillers to achieve higher SEER (in Port bassins for example, at rather low depths) | Reduce electricity consumption of chillers and pumps by replacing existing air cooled or water cooled chillers by more efficient systems in termes of EER) | Large public and private air conditionned office buildings, hotels, hospitals and small scale industries | Eurovent class A SEER from 5,1 to 8 (water cooling) . Hydrocarbon HFC refrigerants only. | Eurovent | Medium term. Sea water cooling can be implemented at low depths (harbor bassins)
B.3.3. | Absorption/adsorption refrigeration Systems considering their high cost of investments (case by case demo projects) and their expected EER | Replace existing water cooled chiller ,to benefit from free energy produced by waste in industrial process or solar heating panels. As far as solar energy conversion is concerned, the EER should be achievable at the required levels through demo projects. | Industrial plants, hotels, hospitals equipped with solar heating panels | Only when free energy is available (heat recovery or solar energy). Back up systems could be necessary . | Eurovent | long term
B.4. | Large range air conditionning systems - cooling towers and Advanced cooling systems
B.4.1. | High efficiency dry cooling tower with high efficiency fans and motors, VSD | Reduce electricity consumption by replacing existing dry cooling tower | Large air conditionning installations with water chiller ; industrial plants, large office buildings, hotels, hospitals | At least IE2 class efficiency motor , VSD | CTI Standards | Medium term | Cooling activities are representing a strategic sector to reduce energy consumption: agrofood industries, commercial facilities and hypermarkets (large scale electricity consumption for cooling). More and more refrigerants as such as R 448 is an option to reduce electricity consumption by 20% and in the same time have GWP ratio under 2500. NH3 (R717) and CO2 (R744) or both combined are the best option to achieve better efficiencies and in the same time targetting low GWP at zero level in fact (natural fluids). Mauritius is expected to be a major market for these new solutions (cleaner refrigerants). Project investments including R 448 fluids are eligible. Project investments including R 717 and/or R 744 (natutal fluids) should be assessed according to their profitability and electricity savings. Information on the investment description should be submitted to the Banks (by project investors and/or their engineering companies, associated in the project design end sizing). This last option (natural fluids) is not yet disseminated at a large scale on the market. The old/previous fluid should be collected and treated adequately to avoid leaks.
B.4.2. | High efficiency evaporative cooling tower , mini IE2 fan motors and VSD | Reduce electricity consumption by replacing existing dry cooling or evaporative tower | Large air conditionning installations with water chiller ; industrial plants, large office buildings, hotels, hospitals | At least IE2 class efficiency motor, VSD | CTI Standards | Medium term
B.4.3. | High efficiency evaporative cooling tower with hybrid condenser , mini IE2 fan motors and VSD | Reduce electricity consumption by replacing existing dry cooling or evaporative tower | Large air conditionning installations with water chiller ; industrial plants, large office buildings, hotels, hospitals | At least IE2 class efficiency motor, VSD (variable speed drive) | CTI Standards | Medium term
B.4.4. | Alternative cooling systems for large scale buildings (commercial malls), agrofood industries and commercial logistics. Choice of refrigerants according to Greenhouse impacts and energy efficiency targets | Using refigerants like the R448a in cooling systems or the NH3 and CO2 refrigerants (natural fluids) to reduce energy consumption by 20% and have a reduced Global Warming Power (ratio: GWP level). Selection criteria refer to comments. | Large scale cooling installations of commercial centres and hypermarkets (60% of total electricity consumption for cooling). Industries in the agrofood sector as the commercial logistics having to retrofit the exiting facilities. | At least increase of 20% of the energy efficiencvy Replacing the polluting fluids such as CFCs, and HFC (R404a and R507a). The range of fluids is quite large. The GWP is the main criteria (base 0: natural fluids) | Acceptable refrigerants according to interational practices and international agreements (use of refrigerents cooling systems) | Short term for activities which should retrofit their factilities urgently to comply with lesgislation objectives on the use of refrigerants Medium term in other cases as Greenfield project (commercial logistics)
B.5. | Pumping equipements
B.5.1. | High efficiency pump (Motor and pump integrated or non integrated) | Replace electricity consumption bu replacing existing pump | For or pumps having a high duration of functioning | at least IE3 class efficiency motor or IE2 class+VSD (variable speed drive) |  | Medium/long term | To justify economically the replacement of pumps, a high annual duration of functioning is necessary (for example, at least 3000 hours per year) ; to justify the setting-up of a VSD (variable speed drive, the operating cycle of pumps has to undergo important variations.
B.6. | Air handling units
B.6.1. | High efficiency air handling unit (AHU) | Reducing electricity consumption by replacing existing AHU | HVAC for large spaces | At least IE2 class efficiency motor equipped withVSD (variable speed drive) | EN 814-2 (E 36-104-2) | Medium/long term | Fans electricity consumption is reduced by high efficiency IE2 motors driven with VSD . In case of a heat recovery handling unit, extracted fresh air cross an heat exchanger to refresh new air and reduce electricity consumption for air conditioning
B.6.2. | Air handling unit with cold recovery | Reducing electricity consumption by replacing existing AHU | Places with high occupation when an important renewal of air is needed | plate heat exchanger or thermal wheel |  | Medium/long term
B.7. | Water chilled water storage (Thermal storage) system
B.7.1. | Cold chilled water storage (thermal storage) systems include regulation devices, supervision equipements…) to have high performance ratio | Store energy produced as free energy at a low cost to postpone its use during the peak hours (peak demand) | Hotels, hospitals and places needing continuous air conditioning | Minimum chilled water capacity of storage : at least 2 hours of nominal hourly production of the main chiller (indicative value) |  | Medium term | Cold chilled water storage is useful in many ways : provide smooth operation and reduce maximum power demand from the chillers, reduce fixed tariff rate, useful for using consumption from PV , for energy storage when continuous air conditionned service is needed (hôtels, hospitals….) Thermal Storage Systems lead to energy saving and smooth operation for the AC system ; if applicable, a new approach could be implemented having additional positive impacts, with the use of PV Systems. This aspect should be encouraged: combining PV systems with high performance chillers, and an equipment to interface both components, called PLC (programmable logic controller).
C. | C. Reduce energy consumption to produce hot water
C.1. | Solar water heaters
C.1.1 | Vaccuum tube collectors. | Produce hot water from solar energy for sanitary or industrial uses. | When domestic hot water is needed (hotels, hospitals, private houses) | EN 12975-1, ISO 9806, EN 12976, EN 12977 | International certification of panels for energy saving (test by certified bodies with EN norms) | Medium term | Install solar water heaters . Replace fuel or electricity ; Energy saving : 800 kWh /m2/year. Evacuated tube collectors offer temperatures of hot water appreciably higher than flat plate collectors, which have however a better global efficiency.
C.1.2. | Flate plate collectors |  | When domestic hot water is needed (hotels, hospitals, private houses) | EN 12975-1, ISO 9806, EN 12976, EN 12977 | International certification of panels for energy saving (test by certified bodies with EN norms) | Medium term
C1,3 | Heat pumps for the production of hot water for households or large scale facilities within the residential sector or hotels | Heat Pumps: producing hot water of households or large scale facilities with high SEER above 4, leading to high electricity efficiency and avoiding constraints linked to large roof surface needed for thermal solar panels | Heat Pumps: Domestic hot water (households) and large scale implementation (hotel sctor) with already case-studies available (hotel sector) | The investment shall not replace existing solar heating device. SCOP ≥ 4,2 which leads to 70-75% of electricity savings (reference: electric water heating) Storage tanks of 150-300 l for households Storage tanks of 2 000 l to 15 000 l for the hotel sector | Eurovent or equivalent international certfication | Meduim term | The hot water can be produced either by electric water heaters which are low investment solutions but relying only on electricity (grid). Solar water heaters widely used in the domestic and houssing sectors have a productivity of 400-600 kWh /m2. The surface constraint for implementing large collective solar collectors is a limiting factor for promoting thermal solar energy. The need to have a monitoring tool for checking in real time the collector productivity is also a strong limitation. The use of heat pumps is a major shift on the market from these technologies to more efficient ones (heat pumlps) which can be ''plug in'' and easily maintained.
C.2. | Heat recovery
C.2.1. | Heat recovery exchanger on chiller condensers. | Recover heat from hot gases before chiller condenser to produce hot water for sanitary or industrial uses | When there is simultaneous need for air conditioning |  |  | Short/ Medium term | Reduce fossil or electrical energy consumption by recuperating free energy on hot gases Chiller units are equipped with desuperheaters and heat exchangers on the discharge line to recover heat from the superheated refrigerant vapour.The recovered heat shall be utilized for pre-heating of the hot water supply.
C.2.2. | Heat recovery on air compressor | Recover heat from hot compressed air to produce hot water for sanitary use | Generally, for the satisfaction of the needs for hot water of the toilets of the staff |  |  | Medium term | Air/water
D. | Improve lighting system efficiency
D.1. | Lamps, fixtures and ballasts
D.1.1. | Led lamps: led downlight fixtures. | Replace lamps and fixtures existing lamps by more efficient and sustainable led equipped devices. | When the durations of lighting are important (commercial premises, halls and circulations in hotels and hospitals) | LED Lighting (Power Density: 2,5 W/m2-100lux) | EU Directive 2005/32/EC | Short/ Medium term | LED replaces gradually the other types of lamps, including compact fluorescent light bulbs, because of their best lighting efficiency on one hand, and of higher life expectancy on the other hand (the quality of the manufacturing is an important factor for this life expectancy. .
D 1,2 | Connected supervision (web) of street lighting systems using LED lamps with real time monitoring | Electricity savings through low energy consumption strategies with LED (lamps) and connected monitoring devices to adapt the lightling power in real time for the best service | Smart cities with new lighting implementation strategy and in urban renewal programmes (on selected sites) | At least 60% electricity savings (reference: existing street lighting systems) | LED lamps (see above) Supervision: advanced monitoring design with references in other countries | Medium term | Upgrading urban lighting systems could be launched in specific conditions: new urban developments such as smart cities with a significant number of lighting systems involved or urban renewal programmes. Pilot projects could be implemented on a few projects as part of a global sustainable approach (sustainable city of the future).
E. | Reduce electricity consumption by monitoring and Control System implementation
E.1. | Lighting , HVAC control system and Advanced Cooling systems
E.1.1. | Occupancy sensors . | Reduce lighting and air conditionning consumption by implementing occupancy control systems | Hotels, offices, corridors |  | CE Marking ; Energy Star Requirements. | Short/ Medium term | Occupancy sensors are generally associated with lighting; can be also associated to ventilation, or air conditioning.
E.1.2. | Energy saving switch for hotel. | Reduce the electric consumption by automatic cut of the supply of the main electrical devices | Hotels |  |  | Short/ Medium term | This device is generally associated with the access in the room (Key Tab)
E.1.3. | Window air Conditioning shut-off Switch | Automatic stop of functioning of air conditioning when windows are opened | Generally for any window in air-conditioned places |  |  | Short/ Medium term | Automatically shut off air conditioning or heating when a monitored door or window remains open for a period of time
E.1.4. | DALI (Digital adressable lighting interface) | Decrease of electricity consumption of electricity by an optimized management of lighting | Mainly for offices or large halls |  | IEC 62386 |  | Reduce lighting consumption by implementing daylighting control system: Energy saving ; variable depends of use ; up to 20 % in best cases Simple to install and commission, a DALI lighting control system can monitor and control lighting within a commercial office environment, which significantly reduces the use ofenergy. Energy costs are lowered through daylight harvesting and standard controls such as dimming and occupancy sensors
E.1.5. | Building management system associated with data collection | Computerized data collection of energy consumption parameters such as flows, electric power, temperatures, pressure in ordrer to manage anf optimize lighting, HVAC and Cooling systems | For any complex air conditioning installation and cooling applications in the commercial centres as an example. |  | CE marked, and; Compatibility to EN 15232 and 15500. | Short/ Medium term | Control and reduce electricity consumption by implementing a building management system : energy savings : variable , up to 20 % in general case
F. Improve energy efficiency of electrical motors and promote renewale energy solutions (PV systems and solar pumps)
F.1 | Electric motors
F.1,1 | High efficiency low voltage motors | Replace existing motors by efficient motor | For electrical motors with a high annual duration of functioning (for example more than 3000 hours per year) | P> 7,5 kW : mini IE3 Premium efficiency class criteria P<7,5 kW, mini IE2 High efficiency class criteria | Standard IEC 60034-30 2009 | Medium/long term | Reduce electricity consumption by replacing electrical motors and implenting VSD (if useful) : energy saving : replacing IE2 with IE3 : up to 20 % for small size motors, up to 10 % for medium size ; implementing VSD : energy saving : depends of the use : up to 30 % in best cases.
F.1,2 | Variable Speed drive for AC induction motors 0,5 kW- 1 MW range | Add Variable speed drive to an existing motor | Economically relevant if the regime of functioning is variable | For electrical motors with a high annual duration of functioning (for example more than 3000 hours per year) | CE marked; • Compatibility to EU EMC 2004/108/EC Directive. | Short/long term
F.1.3 | Variable speed drive for Synchronous motors 0,75kW- 500 Kw | Add Variable speed drive to an existing motor | Economically relevant if the regime of functioning is variable | For electrical motors with a high annual duration of functioning (for example more than 3000 hours per year) | CE marked; • Compatibility to EU EMC 2004/108/EC Directive. | Short/long term
F.2 | PV Solar Systems
F.2.1 | Photovoltaïc Systems with mono/polycrystalline PV panels, thin film panels, inverters, EMS or energy management systems | PV plants on roofs or ground | Ground or roof top applications of different power size from 1-6 Kw households ; 6-100 Small - Medium scale fo both market: s grid feeding systems or auto-consumption systems | Electric efficiency ≥ 15 % Total installed capacity ≤ 100 kWc (mono-polycrystalline panels) | Performance tests IEC 61215, IEC 61730 | Medium term | Replacing fossil energy consumption by solar renewable energy is an increasing solution in Mauritius. Considering the climatic condtions, PV energy recovery is about 1500 kWh / year / KWp,
|  |  |  | Electric efficiency ≥ 15 % Total installed capacity ≤ 100 kWc. (thin films) | Performance tests IEC 61646, IEC 61730 |  | Thin films PV panels are less known than silicon PV panels ; they are however less expensive and their efficiency are less sensitive to ambiant temperature.
|  |  |  | Electric efficiency ≥ 15 % Total installed capacity ≤ 100 kWc. (inversters) | IEC 61 000, IEC 62109, DIN VDE 0126 |  | Inverter is the weak link of the photovoltaic plant in term of life expectancy, (twice less long than the life expectancy of the PV panels.
F 2.2 | PV tracker for small/medium scale projects didn't prove to be beneficial for large projects (benefits/ costs ratio and return of investments) | Small or medium scale if increased energy efficiency is matching overcosts of investments |  | Electric efficiency ≥ 15 % Total installed capacity ≤ 100 kWc. |  |  | Trackers allows a continuous adaptation of the position of the solar panel with regard to the course of sun; the tracker can be monoaxis (to follow the daily course of sun, and bi axis to follow also the seasonal modification of the solar course; monoaxis tracker allows PV panels to reach an annual production of about 1900 kWh / year / Wp considering Mauritius climatic conditions, to compare with static PV pannels production, in ordrer of 1500 kWh / year / Wp. The capacity of resistance of trackers at the cyclonic risk must be taken into account as well as the return of investments (overcosts). Feedback experience not leading to the economic benefits expected.
F.2.3 | High efficiency Solar Pump. | Pomps with PV direct drive |  | Electric efficiency ≥ 15 % Total installed capacity ≤ 100 kWc. |  | Medium term
G. | Improve performance of Compressed air system
G.1. | Compressors
G.1.1. | High efficiency Screw Air Compressor | Replace reciprocating air compressor | For general uses, for workshops and industrial units | High efficiency motor IE2 class + VSD |  | Short/medium term | Reducing electricity consumption by up to 20 % by replacing compressor, dryer and improve compressed air network : potential of energy saving : electricity consumption as usual (7bar): 150 Wh/Nm3 ; consumption with high efficient compressor and efficient network : less than 100 Wh/Nm3
G.2. | Compressed air dryers
G.2.1. | Cycling Refrigerated air dryer or VSD compressor air dryer | Replace air dryer by high efficiency equipment | For industrial uses requiring an medium dry air (dew compressed air: 3°C) | Required air quality class 4 specific consumption ≤ 5 kWh/1000 m3 (air cooled) ≤ 3 kWh/1000 m3 (water cooled) HFC refrigerants only | EU IPPC /BAT/EE ISO 8573-1:2010 | Medium term | Considering the average humidity of the ambient air of Mauritius, drying of compressed air is necessary to protect the devices of condensations, such as pneumatic motors or control valves . Only drying condensation by cold systems allows high flows of air.
G.2.2. | Absorption air dryer | Replace air dryer in case of high quality and low volumes | For medical or food industrial uses requiring a clean and very dry air | Heatless type Required air quality class ≤3 | EU IPPC BAT EE ISO 8573-1:2010 | Medium term | L'adsorption est utilisée pour sécher l'air dans des conditions de haute qualité, exempte de risque de contamination par huile , utilisable ent particulier pour les usages médicaux ; Pour économiser l'énergie de régénération de l'adsorbant, on peut utiliser la chaleur de compression de l'air.
H. | Improve performance of steam production and steam network
H.1. | Boilers
H.1.1. | High efficiency steam boiler | In case of new equipment or boiler house retrofit | For industrial and tertiary uses (laundries of hotel, hospitals) | Net thermal efficiency ≥ 92% | EU IPPC BAT EE ; Council Directive 92/42/EEC ; Council Directive 93/68/EEC ; Directive 2004/8/EC ;Directive 2005/32/EC, • Directive 2008/28/EC | Medium/long term | Efficiency of the steam production system depends mainly on the quality of the exchange between flue gases and steam; Three-pass conventional firetube boiler / wetback design + integrated ecosystem associated to an efficient burner, allows increase of efficiency from 5 to 10 % compared with) a traditional boiler.
H.1.2. | Economiser (Non-condensing) | Add to a standard boiler when a constant régime | To improve the efficiency on industrial boiler rooms working permanently to a high regime | Efficiency by up to 4%. |  | Long term | Water-flue gas heat exchanger for preheating the feeding water, Recovers heat from the boiler exhaust and is used to pre-heat the boiler feed water. This reduces the load on the boiler as the temperature differential of the feed water in the boiler is reduced.
H.1.3. | Condensate recovery system | Recycle condensats in boiler to recover heat. | For manufacturing units using steam in heat exchangers( food-processing, textile industry) | Recovery efficiency 5 to 10 % of fuel energy consumption |  | Medium/long term | Energy contained in the steam condensates represents more than 10 % of the available energy; these condensats are evacuated at high temperature by steam traps ; if they are not polluted, they can be partially sent back in the boiler by an appropriate network.
H.2. | Burners
H.2.1. | High efficiency forced draught type burner | As a replacement of classic ventelle burner | Applicable to any burner of steam or hot water boiler having a high opérating regime | Efficiency up to 3 % of fuel energy consumption and 20% of electricity consumption CO < 40 mg/kWh, NOx≤ 120 mg/kWh Speed-controlled air fan motor, CO/O2 controler | Pressure Equipment Directive 97/23/EC, or CE Marked | Medium term | Burners mix combustive air and fuel (heavy fuel oil, diesel oil, coal or liquefied gas); Quality of this mix is a function of several factors such as viscosity of fuel, pulverizing pressure and temperaturer. Techniques exist to improve the mix such as the steam assisted pulverizing, rotary spin atomizer, the electric consumption of the combustive air fan can be reduced by using an variation speed drive motor ( VSD)
H.2.2. | Oil burner manual or testing kit | To allow a better regulation of burners and an improvement of the burner efficiency | Applicable to any steam or hot water boiler house | Energy saving : variable, up to 1 % of fuel energy consumption |  | Short term | Testing gas burner efficiency during installation and servicing, including CO, Oxygene, smoke test measuring . Associated with an appropriate training of operators, a control and an adjustment of the oxygen quantity in exhaust gases will improve the efficiency of the combustion installation of several points without any investment.
H.3. | Insulation for plumbing and equipment
H.3.1. | Removable insulating pads or valves and fittings | To reduce heat losses of the steam network | Applicable to any steam boiler house | mini 50 mm thickness : Aluminium coated or silicone coated fiber glass or rockwool |  | Short/medium term | For retrofit ; 80 % of energy saving for each fitting
H.3.2. | Fiber glass or foam glass pipe and fitting insulation | To reduce heat losses of the steam network | Applicable to any steam or hot water boiler house | mini 50 mm thickess ; Metal coated fiber glass or rockwool |  | Short/medium term | For steam and condensate recovery network The U.S. DOE estimates that the installation of insulation on valves, pipes, and fittings can reduce steam system energy use by 1-3% (U.S. DOE 2006c).
I. | General process equipments
I.1. | Fan
I.1.1. | High efficiency fan | Replace or retrofit of fans on industrial installations or HVAC | Applicable to high power fans and boosters in industry sector and cooling towers | at least IE3 class efficiency motor or IE2 class + VSD |  | Short/medium term | Improvement of fans energy efficiency depends on efficiency on electrical motors, implementation of variable speed drive and technological arrangements(blades in fiberglass, plug fans
I.2. | Pump
I.2.1. | High efficiency pump | Replace or retrofit of pumps on industrial installations or HVAC | Applicable to pumps for ice water networks, and cooling loops, as well as to the pumps for diverse uses in industry. | At least IE 2 class efficiency motor + VSD |  | Medium/long term | Most of the industrial processes need variable flows of fluids according to the conditions of production; flow variation produced by variable speed drive motor replaces advantageously flow adjustment by control valve in term of energy efficiency.
I.3. | Heat pump
I.3.1. | High efficient heat pump | Production of hot water for sanitary or industrial use | For the production of medium-temperature hot water in the industry, and for the production of domestic hot water in the hotels and the hospitals | COP ≥ 5.10 5 (water to water type) COP ≥ 3.8 (air to water type) | European Heat Pump Association |  | Production of hot water by heat pump is a competitive alternative in production of hot water by diesel oil boilers. Associated with photovoltaic panels, heat pump can be an alternative in solar water heaters.
I.4. | Sensors and metering
I.4.1. | Pressure, Temperature, Humidity, Mass flow rate, power, lumens. These sensors will be used for data collection and energy performance contracting | Optimization of the energy use of equipments for monitoring objectives in the frame of energy performance schemes or energy management approaches | Applicable to all industrial processes and tertiary sectors considered as intensive energy consumers |  | CE marked ; Compatibility to EN 15500 |  | Appropriate measurement of thermal or hydraulic processes is essential befort their energy optimization.
J | Specific Process equipments
J.1. | Coolrooms, refrigerated showcases and display cabinets
J.1.1. | High efficiency coolrooms, refrigerated showcases and display cabinets | Reduction of electricity consumption by more efficient new equipements | Applicable to all food stores and food cold rooms | Including reinforced wall and roof insulation, double glazing doors, high efficiency compressors and fans (VSD drive, electronic commuted), high efficiency led lighting |  | Short term | The performances of cold rooms and food displays with positive or negative temperature strongly progressed, as long at the level of the production of cold, that the envelope and the equipments. Energy savings produced by effective modern equipments are more than 30 % with regard to classic food stores equipments.
J.1.2. | Reinforced wall and roof insulation | Reduction of electricity consumption by retrofit of equipements | Applicable to cold rooms |  |  | Medium/Long term | The strengthening of the insulation of walls allows a long-lasting economy.
J.1.3. | Night blinds | Reduction of electricity consumption by retrofit of equipements | Applicable to food displays |  |  | Short term | The implementation of night-curtains on the displays cooled in positive temperature is an immediately profitable measure.
K | Renewable Energy: hydroelectricity
K.1. | Micro / pico- hydroelectricity
K.1.1. | Hydroelectric turbine Power of a few KW (pico) or up to 100 kW generators, alternators, EMS (energy management systems) | Increase of the production by retrofit or replacement of equipments |  | Efficiency > 80% and 85% on generators and alternators | IEC 1116 (Electromechanical equipement Guidefor small installations) | Medium/Long term | Total installed capacity ≤ 100kW per unit installed
IEC 60034 IEC 1116 (Electromechanical equipement Guidefor small installations)
L | Urban Street furniture and PV systems for new services
L 1 | Sustainable street furniture web-connected and with PV powered associated to battery storage | Provide new neigborhood services with PV powered urban furniture not connected to the grid (E-Tree concept) | Charging smart phones or computers, water supply, lighting at night (LED), WIFI services with PC powered furnitures (1,5 to 7 kW per urban furniture) | PV panels should comply with the performance specifiactions (F 2,1) and lighting with LED adapted to this local application | PV panels (see F 2,1) and LED (D 1,1) | Medium/Long term | Private companies which are very active promoting new services on the market (urban furnitures) should be interested to promopte PV powered systems providing new services to the public on specific places (smart cities, university campus, business centres like ''Ebène'', or renewed urban districts. Pilot projects could be launched to check the public acceptance of these new services.
M | E- Mobility solutions for companies, transport operators and leasing companies
M 1 | E Mobility developed by companies and transport operators | Introduce E mobility solutions for large scale applications excluding households | Transport, Industrial and leasing companies | Renewable Energy coverage of charging needs (power) with minimum of 20 kW for a fleet of corporate vehicules (charging point power of 20 kW and installed solar PV of 20 kW minimum). PV system has to be connected to the grid via MSDG or 100% off-grid. For residential, ONLY through leasing companies, PV system has to be connected to the grid via SSDG or 100% off-grid Type of vehices: cars, vans and minibuses. An electric car < 180 kw is eligible. All cars > 180 kW are considered as luxurious cars | Charging stations: EU specifications | Medium / Long term | Eligible equipments: electric véhicles and charging stations with several options: as Option 1 Entire Package véhicles/ charging station , Option 2: separate lots (different suppliers) Charging station of several vehicles could be along "slow" charging mode or "semi-fast" charging mode. Typical charger are 3-phase 22kW (an example) Power for charging will differ according to the number of vehicles, types of vehicles and the charging modes Battery technology could be Li-Ion or NiCd or other technologies approved by certification bodies PV panels, inverters are part of the grid connected projects (SSDG, MSDG, off-grid) eligible as well to SUNREF financing.
Note 1 : The LEME is an evolutive document and updated versions will be released as and when deemed required by the Technical Assistance (TA) team in agreement with AFD. Potential beneficiaries are advised to check with their Partner Bank to ensure they are using the latest version. Note 2 : The LEME is not an exhaustive list. An item not listed in the LEME does not necessarily imply that it is excluded from SUNREF III financing programme. In the event that items which are deemed to be potentially eligible are not referenced in the LEME, 1.) potential beneficiaries are advised to check with their Partner Bank on the best way forward and 2.) suppliers are encouraged to contact the TA team on the following address : sunrefmaurice3@aets-consultants.com